## Slide 1
1. INTRODUCTION
Numerical investigation of thermal stratification in horizontal solar water tank
Qiong Li, Wenfeng Gao*, Wenxian Lin
Solar Energy Research Institute, Yunnan Normal University, Kunming, Yunnan 650500, China liqiong@ynnu.edu.cn
4. CONCLUSION
The transient thermal stratification of solar water tank is simulated by CFD, the results showed the temperature stratification in water tank dynamically.
When solar water heating system is in the heating state, the high temperature water rises to the top of the water tank, and the low temperature water sinks to the bottom of the water tank, thus forming different degrees of thermal stratification in the heat storage tank. Reasonable use of the thermal stratification of water tank can reduce the inlet temperature of solar collector and improve the efficiency of the collector. It can also increase the high temperature water that can be used, so as to improve the system efficiency of solar energy utilization [1,2].
2. METHODS
ABSTRACT
3. RESULTS AND DISCUSSION
Alternative Energy Sources, Materials & Technologies (AESMT’20)
The internal structure of solar water tank has important influence on thermal stratification of hot water. A partitioned solar water storage tank is proposed, and the water mixing of the tank is analyzed by computational fluid dynamics (CFD). The cold water inlet velocity of the solar water tank is 0.14 m/s, and the effect of partition on thermal stratification was studied. The results showed that the thermal stratification effect of water tank with partition is better than that without partition, but the heat release effects of the water tank need to be depth analysis..
The commonly used horizontal cylindrical water tank in solar water heating system is equipped with 2 partitions at equal intervals, and its appearance is shown in Fig.1. The diameter of the water tank is 0.4 m, the length is 1m, and the diameter of both inlet and outlet pipes is 0.02 m. The diameter of the partition is the same as that of the water tank, and there is a round hole with a diameter of 0.025 m at a distance of 0.04 m from the bottom. The partition shall be cut off horizontally 0.05 m from the top of the tank.
Fig.1. Schematic diagram of horizontal solar water tank with partition.
1. Numerical analysis
Take the solar water storage tank shown in Fig.1 as the research object for numerical simulation, the internal temperature stratification of the water-proof stage is studied. According to the actual flow, set the inlet velocity at a low speed of 0.14 m/s, the hot water temperature in the tank as 333k, the cold water inlet temperature as 293k, and no stratification of the initial water temperature in the tank.
2. Characteristic parameters of solar water tank
The dimensionless exergy proposed by Rosen [4] is used to quantitatively analyze the characteristics of the thermal stratified water in hot water storage tank. The expression of fluid instantaneous exergy in the tank is as follows:
1. Observation
Cold water enters the bottom of the inlet silo through the inlet and is mixed with internal hot water. When the blending height is higher than the round hole under the left partition, it starts flowing into the bottom of the middle silo. Over time, the blending height began to rise in the middle silo and entered the bottom of the water outlet silo through the round hole on the right side of the partition. Since then, cold water has been mixed with hot water in each silo. When the mixing height of the water inlet silo is higher than the height of the left partition, cold water starts to flow into the middle silo from the silo roof. With the development of time, the cold water blended in the middle silo then began to flow into the outlet silo from above the right partition.
2. Parameter analysis
The temperature at the centre of the partition hole is monitored. It can be seen from Fig.2 that the duration of the high temperature of the non-division tank in the initial stage is slightly longer than that of the partitioned tank, but the temperature of partitioned tank is higher in the steady state.
Fig.2. The water discharge curves of tanks at 0.14 m/s.
It can be seen from Fig.3 that the initial blending degree of the non-division tank is relatively larger, and then it gradually decreases. The blending degree of partitioned tank is lower throughout the process, indicating that partitioned tank has the better stratification at a flow rate of 0.14 m/s.
Fig.3. Dimensionless exergy values of both tanks at an inlet velocity of 0.14 m/s.